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Asset Protection:
Water Main up to 250mm diameter  
No building temporary or permanent is permitted above the water main or within 6 metre over the main, 3 metre on either side of the centre line of the pipe.

We require detailed plans and the construction depths of the proposed works.  Prior to work commencing you are required to confirm the line and level of the water main in the location of the works through hand dug trial holes.  Please be aware of the following precautions and requirements in consideration of your planned works: 

1. Main and easement not to be located within the confines of property boundaries.
1. Main to be located in green public open space or adoptable public highway.
1. No machine excavation within 1000mm of the pipe, subject to confirmation of location. Within 1000mm all excavation undertaken by hand.
1. No excessive ground is to be removed from the surround of the pipe. 
1. No excessive ground is to be removed below crown of pipe, angle of repose to remain at 30° any works beyond this are prohibited. Further consultation will be required. 
1. No ground is to be removed surrounding bends or thrust blocks.
1. At no point or time will the pipe be undermined.
1. At no point will joints to the pipe be exposed.
1. No heavy plant is to cross the main unless there is a designated crossing point.
1. Point loadings of plant and equipment are to be supplied.
1. Details of protection measures to protect the asset to be supplied.
1. Details of how the protection measures will be constructed and maintained.
1. Detailed design and construction method statement taking into consideration everything detailed herein.
1. No directional drilling.
1. No piling and drilling within 6000mm of the pipe without approval. Vibration monitoring will be required as a result of any such undertaking.
1. Contingency plans in the event that you do damage the pipe.
1. Sequence of works.
1. No other apparatus is to be laid within 300mm of our apparatus either above or below -subject to review of your detailed plans and STW agreement. 
1. All service crossings to be laid at 90° and to be ducted.
1. Storm and foul construction details to be supplied with applicable method of construction.
1. No manholes / gullies permitted within 3 metre on either side of the pipe.
1. Full details of any demolition proposed.
1. Street lighting details to be provided.
1. Full information on any earth /noise bunds proposed
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Cautionary notes for your consideration:

1. The contractor/company is to ensure he has adequate insurance in the event of consequential damage.  STW will look to recover all associated costs thereof in the event of damage and loss. 
1. The Health and Safety pack for the site must have Severn Trent Water details within in the event of an emergency.  0800 783 4444
1. Any designer or Architect designing works in the vicinity should ensure the above is accounted for and detailed accordingly.
1. Every possible precaution should be taken to avoid damage to our apparatus. You or your contractor must ensure the safety of our equipment and will be responsible for the cost of repairing any damage caused.

Planting:

What type of planting is proposed? Trees and shrubs that have deep root ball growth are best thereby ensuring root growth around the main is avoided. We would be happy to review any planting proposed once they are available. We would also prefer that tree canopies do not develop over the main thereby ensuring that interference above ground is avoided. The following guidance should help to avoid such a scenario developing:

1. Poplar and willow trees have extensive root systems and should not be planted within 12  metres of a STW asset;
1. No large or forest trees should be planted within 10 metres of a STW asset. (Examples include oak, ash, beech, sitka spruce, douglas fir etc.);
1. Medium and small size trees should be planted in such a way as to ensure that the eventual root spread reaches no closer than 1 metre to the asset. In practice, if trees are planted a distance of 6 metres away from the pipeline this should be sufficient;
1. When simple screening is required within 2m of a STW asset, the following shallow rooting shrubs would be suitable: blackthorn, broom, cotoneaster, elder, hazel, laurel, privet, quickthorn, snowberry, and most ornamental flowering shrubs.
1. STW requires access to the route of its mains at all times to inspect for leaks and carry out surveys. Shrubs or bushes which might obstruct or interfere with our access should not be planted within 1metre of the centre line of any water main. However, in areas where soft fruit is grown, blackcurrant, raspberries and gooseberries may be planted close to the main, provided that a path is left clear for inspection access and surveys.

The measurements and distances set out above are for guidance only and there will always be exceptions. If you are unsure in any individual case, then specialist advice should always be sought prior to planting and discussed with STW.

Prior to planting commencing, appropriate on site apparatus detection techniques should be employed, and trial holes should be undertaken to validate the results of such detection surveys to confirm the actual position and depth of the apparatus.

Any damage to STW’s assets caused by inappropriate planting by a third party must be rectified at the cost of that third party.



On completion:
1. Maintained access and egress. To enable suitable plant and equipment to repair, renew or maintain the asset.
1. Consideration given to height and width access.
1. Consideration given to the working environment in the event of repair and maintenance. 
1. Handover and inspection.  
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