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	Jessica Clarke-Roome
Planning Services 
South Derbyshire District Council
Civic Offices
Swadlincote 
Derbyshire
DE11 0AH

	Telephone
	01629 532798

	
	Ask for
	Sam Morgan

	
	Email
	Sam.morgan@derbyshire.gov.uk

	
	Our ref
	SDDC/2025/32

	
	Your ref
	DMOT/2022/0251

	
	Date
	22 September 2025
	
	
	



	Dear Jessica

	Proposal:
	Approval of details required by conditions 8 (Salt Brook bridge crossing details), 10 (Construction Method Statement) and 11 (Sustainable drainage assessment) attached to ref. DMPA/2020/0521 (The variation of conditions nos. 2, 5, 8, 10, 18, 19, 20 and 45 and removal of conditions nos. 7 and 9 of permission ref. 9/2015/1108 to facilitate amendments to road alignments, updating of housetypes, re-planning of plot layouts and to accommodate previous approvals of details required by conditions (relating to the demolition of the existing residential property (Cherry Cottage) and agricultural barn and development for 385 residential dwellings (use class C3), formal and informal public open spaces, structural landscaping, new roads, footpaths and cycleways, 2 no. site accesses and ancillary works)) on Land at SK2130 8875, South of Derby Road, Hatton, Derby.

	Location:
	Land at SK2130 8875, South of Derby Road, Hatton, Derby

	Application reference
	DMOT/2022/0251



OBJECTION TO DISCHARGE OF CONDITIONS 10 (Construction Method Statement) and 11 (Sustainable Drainage Assessment)
Derbyshire County Council as the Lead Local Flood Authority (LLFA) has reviewed the information submitted for this application, which was received on 26/02/2025. The LLFA has NOT received information that satisfies the condition under consideration and cannot therefore recommend its discharge.
A summary of review of information required for the Discharge of Conditions for DMOT/2022/0251 is provided below:
· Condition 10 (Construction Method Statement) and 11 (Sustainable drainage assessment) Insufficient detail has been provided for discharge of this condition, and we therefore cannot recommend its discharge. Further site-specific comments are provided below.

Specific comments relating to Conditions 10 and 11 are as follows, (relating to the further information requested by the LLFA 04/12/2024: 
· Detailed design of the proposed 7 No. ponds to be provided in accordance with CIRIA SuDS manual C753, for the proposed pond, a plan and cross sections are required showing gradients of slopes, permanent water level, maximum water level for storms up to 100 year plus 40% climate change, other details such as freeboard and outlet details (CIRIA SuDS Manual C753). 
· Regarding the drawings of the 7 ponds, the maximum water levels provided are for a 100 + 30% climate change event, this should be a 40% climate change event. 
· Cross Section drawings not provided.

· Latest version of the Engineers Layout drawings to be submitted.
· 2 balancing ponds are labelled as pond no.3. Should the one lower down the site be labelled no.5?

· No document has been submitted in support of condition No 10 (Construction Method Statement).
· [bookmark: _Hlk209446703]Whilst a number of construction method statements have been provided in the headwall drawing notes, could the applicant provide a document with these all combined? Construction management details should also be provided for all other elements constructed such as drainage basins and surface water sewers. 

· The applicant has not submitted the Microdrainage results for the 1 in 100 year design storm including 40% climate change, these calculations need to be submitted for all of the 7 areas.
· Applicant has used CV Values of 0.750 and 0.840. These should be set to 1.
· Only areas 1-4 provided.

· Can the applicant resubmit Microdrainge results for the most critical duration of storm event 1 in 30 year design storm for all of the 7 areas.
· Applicant has used C levels of 0.750 and 0.840. These should be set to 1. 
· Only areas 1-4 provided.

· Applicant to provide details indicating how additional surface water run-off from the site will be avoided during the construction phase. The applicant may be required to provide collection, balancing and/or settlement systems for these flows. The approved system shall be operating to the satisfaction of the LPA, before the commencement of any works, which would lead to increased surface water run-off from site during the construction phase.
· Please can the applicant provide a separate individual document providing how additional surface water run-off from the site will be avoided during the construction phase. This should be for all elements constructed.



	Yours sincerely
	

	

	Sam Morgan

	Flood Risk Technician 

	

	Checked by:
	Martin Coleman

	Date
	23/09/2025
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